| Custom Label Sheet | CLS1 |
| --- | --- |

| ALU or GSU |  | (if GSU then go to bottom half of sheet) |
| --- | --- | --- |

ALU Label Requirements

CHANNEL            BACKGROUND STYLE	                          FONT STYLE	                   FONT COLOUR       (Use our Website for Examples and Descriptions)

(White = Standard)		               (Standard = Standard)		      (Dark Blue = Standard)

| 1 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| 2 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| 3 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| 4 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| 5 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| 6 |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

If you also require a Unit Identification Label please enter the details below

| IDENTIFICATION |  | BACKGROUND STYLE |  | FONT STYLE |  | FONT COLOUR |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

(If Required, None = Standard)

GSU Label Requirements

If you are requiring to make a change to an alarm identification label please use the GSU configuration Sheet to make your change to an Alarm Name, We will then apply a label onto your required alarm input window which will have a matching white background with standard font in dark blue

Things to take into consideration before making any name changes to the standard Alarm Labels . . .

Channel 1 ‘High Delivery’ this is a Shutdown Alarm that only acts in Service Mode (indication ONLY in Purge Mode)

Channel 2 ‘Extract Fail’ this is a Shutdown Alarm that has a user adjustable 1-10 second delay and acts in Service Mode and Purge Mode

Channel 3 ‘Excess Flow’ this is a Shutdown Alarm that has a fixed 6 second delay that only acts in Service Mode (indication ONLY in Purge Mode)

Channel 4 ‘Low Cylinder’ this is a Warning Alarm which will not close the valve when active that is indication ONLY in Purge Mode

Channel 5 ‘Aux’ this is a Shutdown Alarm that acts in Service Mode and Purge Mode

If you also require a Unit Identification Label please enter the details below

| IDENTIFICATION |  | BACKGROUND STYLE |  | FONT STYLE |  | FONT COLOUR |  |
| --- | --- | --- | --- | --- | --- | --- | --- |

(If Required, None = Standard)

| Additional Notes |  |
| --- | --- |

| Configuration Sheet Completed By : |  | Date : |  |
| --- | --- | --- | --- |